## Comparison
Stejaru HPP — DN500 PN10 Regulating Valves — Supplier Comparison
Project 740142 Stejaru 2025 ¦ Scope: 2 pcs bypass/filling (NP-3192923) + 1 pc drain/dewatering (NP-3192920) = 3 valves ¦ Prepared 03-Jul-2026
Criterion | Tender requirement | VAG (RIKO) | AVK / ACMO (S872) | Rheintal (PLUVA) — 1st | Rheintal (PLUVA) — 2nd
|  | 1st offer 27-May-2026 | Budgetary 24-Jun-2026 | 1st offer 23-Jun-2026 | Revised 03-Jul-2026
TECHNICAL
Product / type | Plunger / needle / conical control valve (RIKO type indicated) | RIKO EP DN500 — type E (drain) / SZ 25 (bypass) | AVK series 872 needle valve (mfr ACMO) | PLUVA-15-0500 plunger valve | PLUVA-15-0500 plunger valve
Quantity | 3 (2 bypass + 1 drain) | ✗ 4 quoted (drain 2 vs 1) | ✓ 3 | ✗ 2 quoted (under by 1) | ✓ 3
Body material | Steel (NP; Annex 3.1 §3.5; Vol 3 Pt2 §4.3.5) | ✗ EN-GJS-350-22 ductile iron — derogation | ✗ EN-GJS-500-7 ductile iron — derogation | ✗ GGG50 ductile iron — derogation | ✓ ASTM A216 WCB cast steel
Internals | Closure member + spindle stainless steel | ✓ 1.4301 / 1.4057 | ✓ 1.4301 / 1.4028 | ✓ CF8 / F51 duplex | ✓ CF8 / F51 duplex
Actuator | Electric, self-locking, ≤60 s, 4-20 mA, IP68, manual override | ✓ Auma SAR 07.6 + AUMATIC AC 01.2 | ✓ Auma SAR, RWG 4-20 mA, IP68 | ✗ Gearbox + handwheel only | ✓* Auma SA actuators confirmed — price addendum pending
Cavitation / trim | Cavitation-free over full range (64→0 m w.c.) | type E multi-stage + air-venting (drain) | air-intake / anti-cav cylinder (drain case) | ✗ 0.2 bar ΔP, 0 cages | ✓ 3-stage cage trim, both duties, ΔP 6.28 bar (REV1)
Sizing basis | Real duty; 64 m head; bypass v=4, drain v=2.5 m/s | type E / SZ 25 per duty | ⚠ only drain case (2.5 m/s) | ✗ 0.2 bar placeholder only | ✓ both cases at ΔP 6.28 bar (REV1)
Flanges | Form H per EN 1092-1, countersunk, f4=4.5 mm (CKD-52844) | ✓ form H, countersunk | ✓ form H, z h10, f4=4.5 | ✗ EN 1092-2 RF | ✓* form H confirmed (quote still shows RF — to reissue)
Inclined ~35° (bypass) | 2 bypass valves in rising pipe ~35° | no restriction stated | ⚠ to confirm (horizontal assumed) | ✗ 'not permissible' | ✓* confirmed (no detail of measures)
Operating temp | −25 °C to +30 °C | actuator −40/+80; freezing caveat | TPU seat / FBE — confirm sub-zero | ⚠ sub-zero not addressed | ✓* suitable −25/+30; no anti-freeze provision
Seismic | P 100-1/2013, a_g=0.20 g, T_C=0.7 s, class II | ✗ not addressed | ✓ full report; anchor ≈1.0 kN | ✗ not addressed | ✓* confirmed in email (no report yet)
Coating | W=510 / A=310 µm (CKD.740 142-04) or mfr system by agreement | 300 µm RAL 5005 | ✓ 'special coating 510 µm' RAL 5017 | ⚠ 250 µm FBE | ⚠ RAL 5005 confirmed; thickness 510/310 not confirmed
COMMERCIAL & CONTRACTUAL
Guarantee | 5 years (Annex 3.2 §4.1; corrosion ≥5 yr §8.10) | ✗ 24 months | ✗ 2 years | ✗ not stated | ✗ not confirmed (only colour answered)
Documentation | Romanian/English (+ Czech); EN 12266 tests, EU DoI | requested RO/EN/CZ (to confirm) | 3.1 certs; no third-party test ⚠ | not specified | ⚠ English only
Delivery time | Contract delivery June 2027 | 30 weeks | 22–24 weeks | — | TBC (Auma 1-2 wk to quote)
Terms | — | EXW Hodonín; payment in advance | EXW Skovby (DK); terms TBD | EXW Willich / self-pickup; +2% packing | EXW Willich / self-pickup; +2% packing
Offer validity / status | — | Firm; valid to 27-Jun-2026 (EXPIRED — extend) | Budgetary (indicative) | Superseded by 2nd offer | Revised; valid to 23-Jul-2026; addendum pending
PRICE — normalised to required 3 valves (EUR, net, ex works)
Line | Qty | VAG €/unit | AVK €/unit | Rheintal 1st €/unit | Rheintal 2nd €/unit
Drain / dewatering (NP-3192920) | 1 | 54035.33 | 17472.96 | 12881.73 | 23398
Bypass / filling (NP-3192923) | 2 | 45640.05 | 17472.96 | 12881.73 | 23398
TOTAL — 3 valves | 3 | 145315.43 | 52418.88 | 38645.19 | 70194
Scope of price |  | incl. electric actuators + drain air-venting | incl. electric actuators (budgetary) | GEARBOX ONLY; iron body; as quoted 2 valves = €25,763 (30% disc) | GEARBOX ONLY — actuators not yet priced; steel body
Legend: | Conforms | Partial / open / to confirm | Non-conform / deviation | * email-confirmed (Rheintal) | Blue=input, black=formula
Notes:
* Rheintal 2nd-offer items marked with an asterisk (actuator, flanges, inclined install, temperature, seismic) were confirmed in their email of 03-Jul-2026 but are NOT yet reflected in the formal written quotation — they must be captured in a reissued quote/order confirmation to be binding.
• Body material: all three FIRST offers were ductile cast iron (uniform derogation handled). Rheintal's 2nd offer switched to WCB cast steel and now meets the tender as written.
• VAG total shown corrected to the required 3 valves (drain 1, bypass 2); as originally quoted VAG = 4 valves = €199,350.77.
• Rheintal totals are GEARBOX-ONLY. 1st offer €38,645 normalised (actually quoted 2 valves = €25,763, 30% disc). 2nd offer €70,194 (steel body, discount removed); Auma actuator addendum still to come and will raise it.
• AVK is a budgetary (indicative) offer; firm price + validity still to be requested. Open: 35° install, bypass (4 m/s) sizing, 5-yr guarantee, witnessed testing.
• Rheintal open items for formal offer: reissue clean quote (still shows EN 1092-2 RF / 'inclined not permissible' / 250 µm), Auma actuator price, 5-yr guarantee, coating 510/310 µm, RO/CZ documentation.